Specification for Ultrasonic Testing of Piles

1. Introduction: For ultrasonic testing at least two steel or PVC tubes are cast in the pile. An ultrasonic  transmitter is lowered in one of the tubes and a receiver - in the other. Both transducers are connected to a computer that plots the time of first arrival versus depth.  As long as this time is approximately constant the pile is considered acceptable. If, on the other hand, a late arrival is recorded at any depth it means that the concrete between the tubes is defective at this level. Installing a larger number of piles along the perimeter of the piles will provide almost complete coverage of the cross-section.

2. Testing agency: The ultrasonic test shall be carried out by a firm experienced in this kind of work and approved by the Engineer. Both site work and interpretation of the results shall be carried out by a Geotechnical engineer with proven experience.

3. Equipment: The test  shall be performed using a computerized system of reputable origin. All components shall be recently calibrated and in good working order. All software shall be of the latest released version.

4. Piles to be tested: All piles shall be tested at a minimum age of five days after casting, unless instructions to the contrary shall be given by The Engineer.

5. Test tubes: All tubes shall be new, straight  and clean both inside and outside, with a minimum internal diameter of 50 mm. All connections shall be welded externally, taking care that no welding material penetrates inside. Both ends of the tube shall be closed with welded steel discs. The Contractor shall take all due care to avoid any damage to the tubes during manufacturing, installation, concreting and the trimming of the head.

6. Preparation for testing: Before commencing the test, the Contractor shall ensure that there is adequate access to  the pile. The Contractor shall use a disc saw to cut the top of the test tubes cleanly at a level of 200 to 300 mm above the  concrete, unless ordered otherwise. The tubes shall then be tested for access throughout their length using a 1” tube as a dummy. Having passed this test, the tubes shall be completely filled with water.

7. Reporting: A final report for each testing stage shall be presented not later that three working days after completion of that stage. The report shall consist of a printout of the original output, as well a summary table including, for every pile tested, the depth and The Engineers' interpretation regarding its integrity.

For more help with this paper click here